Tender Specification Filter  Isolation Amplifier DB 6230

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Filter Isolation Amplifier, selectable cut-off frequency, Zero/Span compensation, simple signal setting

Isolation and conversion of industrial signals with configurable filter function,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input				± 20 mA, ± 10 mA, 0 - 20 mA, 4 - 20 mA, 0 - 10 mA, 2 - 10 mA
				± 10 V, ± 5 V, 0 - 10 V, 2 - 10 V, 0 - 5 V, 1 - 5 V
Output				± 20 mA, 0 - 20 mA, ± 10 V, 0 - 10 V 
Range setting			simple selectable via DIP switches

Subsequent readjustment	zero/span potentiometers on the front panel

Filter function			Cut-off frequency 10 Hz, 1 Hz, 0.5 Hz or 0.1 Hz switchable

Transmission error		< 0.1 % full scale

Power Supply			Universal power supply for 20 - 253 V AC/DC

Protective separation		EN 61140, 3-Port isolation up to 600 V AC/DC between all circuits

Test voltage			4 kV, 50 Hz, 1 min., input against output against power supply

Working voltage		1000 V AC/DC for overvoltage category II and pollution degree 2

Type				Filter Isolation Amplifier DB 6230 AG – __ – __  	
								(customer spec. default setting, see order code)

Supplier			DRAGO Automation GmbH, Berlin, Germany

Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code for customer specific settings:

|  |  | Input |  | Output |
| --- | --- | --- | --- | --- |
| DB 6230 AG – |  | XX | – | YY |
| ± 10 V |  | 00 |  | 00 |
| 0 - 10 V |  | 01 |  | 01 |
| 2 - 10 V |  | 02 |  |  |
| ± 5 V |  | 03 |  |  |
| 0 - 5 V |  | 04 |  |  |
| 1 - 5 V |  | 05 |  |  |
| ± 20 mA |  | 06 |  | 06 |
| 0 - 20 mA |  | 07 |  | 07 |
| 4 - 20 mA |  | 08 |  |  |
| ± 10 mA |  | 09 |  |  |
| 0 - 10 mA |  | 10 |  |  |
| 2 - 10 mA |  | 11 |  |  |

Bold: Default setting, if no information is given by ordering