Tender Specification Passive Isolator DH 1000

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

4 versions available:

Passive Isolator, 1 channel

Separation of 0(4) - 20 mA standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			0(4) - 20 mA
			Voltage drop < 2.0 V
			Overload ≤ 100 mA, 30 V

Output			0(4) - 20 mA

Load 500 Ohm

Transmission error	< 0.1 % full scale

Power supply		None, the power is derived from the measurement signal

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between input and output

Test voltage		1.5 kV, 50 Hz, 1 min., between all circuits

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Passive Isolator DH 1011 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-30-409982-0, Fax: +49-30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Passive Isolator, 2 channel

Separation of 0(4) - 20 mA standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			2 x 0(4) - 20 mA
			Voltage drop < 2.0 V
			Overload ≤ 100 mA, 30 V

Output			2 x 0(4) - 20 mA

Load 500 Ohm

Transmission error	< 0.1 % full scale

Power supply		None, the power is derived from the measurement signal

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between input and output

Test voltage		1.5 kV, 50 Hz, 1 min., between all circuits

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Passive Isolator DH 1012 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-30-409982-0, Fax: +49-30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Passive Isolator, 1 channel, protective separation, test voltage 4 kV

Separation of 0(4) - 20 mA standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			0(4) - 20 mA

Voltage drop < 2.0 V

Overload ≤ 100 mA, 30 V

Output			0(4) - 20 mA

Load 500 Ohm

Transmission error	< 0.1 % full scale

Power supply		None, the power is derived from the measurement signal

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		4 kV, 50 Hz, 1 min., between all circuits

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Passive Isolator DH 1021 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-30-409982-0, Fax: +49-30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Passive Isolator, 2 channel, protective separation, test voltage 4 kV

Separation of 0(4) - 20 mA standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			2 x 0(4) - 20 mA

Voltage drop < 2.0 V

Overload ≤ 100 mA, 30 V

Output			2 x 0(4) - 20 mA

Load 500 Ohm

Transmission error	< 0.1 % full scale

Power supply		None, the power is derived from the measurement signal

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		4 kV, 50 Hz, 1 min., between all circuits

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Passive Isolator DH 1022 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-30-409982-0, Fax: +49-30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent