Tender Specification Loop-Powered Isolator DH 11000

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

2 versions available:

Loop-Powered Isolator, 1 channel

Separation of 0(4) - 20 mA standard signals,

slim housing for DIN-rail mounting, width 6.2 mm, protection class: IP 20

Input				0(4) - 20 mA
				Voltage drop < 2.3 V
				Overload ≤ 50 mA, 30 V

Output				0(4) - 20 mA

Load 600 Ohm

Transmission error		< 0.1 % full scale

Cut-off frequency		100 Hz

Power supply			None, the power is derived from the measurement signal

Protective separation		EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage			3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage		600 V AC/DC for overvoltage category II and pollution degree 2

Type				Loop-Powered Isolator DH 11010 S

Supplier			DRAGO Automation GmbH, Berlin, Germany
				Phone: +49-30-409982-0, Fax: +49-30-409982-10, 
				email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Loop-Powered Isolator, 2 channel

Separation of 0(4) - 20 mA standard signals,

slim housing for DIN-rail mounting, width 6.2 mm, protection class: IP 20

Input				2 x 0(4) - 20 mA

Voltage drop < 2.3 V

Overload ≤ 50 mA, 30 V

Output				2 x 0(4) - 20 mA

Load 600 Ohm

Transmission error		< 0.1 % full scale

Cut-off frequency		100 Hz

Power supply			None, the power is derived from the measurement signal

Protective separation		EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage			3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage		600 V AC/DC for overvoltage category II and pollution degree 2

Type				Loop-Powered Isolator DH 11020 S

Supplier			DRAGO Automation GmbH, Berlin, Germany
				Phone: +49-30-409982-0, Fax: +49-30-409982-10, 
				email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent