Tender Specification Passive Isolator DH 18

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

2 versions available:

Passive Isolator, 1 channel

Separation of 0(4) - 20 mA standard signals,

slim housing for DIN-rail mounting, installation depth 60 mm, width 11.2 mm, protection class: IP 20

Input			0(4) - 20 mA
			Voltage drop < 3.0 V
			Overload ≤ 50 mA, 15 V

Output			0(4) - 20 mA

Load < 600 Ohm

Transmission error	< 0.1 % full scale

Operation temeprature	–20 °C to +60 °C   (–4 °F to +140 °F)

Power supply		None, the power is derived from the measurement signal

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Passive Isolator DH 18 P–1

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-30-409982-0, Fax: +49-30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Passive Isolator, 2 channel

Separation of two 0(4) - 20 mA standard signals,

slim housing for DIN-rail mounting, installation depth 60 mm, width 11.2 mm, protection class: IP 20

Input			2 x 0(4) - 20 mA
			Voltage drop < 3.0 V

Overload ≤ 50 mA, 15 V

Output			2 x 0(4) - 20 mA

Load < 600 Ohm

Transmission error	< 0.1 % full scale

Operation temeprature	–20 °C to +60 °C   (–4 °F to +140 °F)

Power supply		None, the power is derived from the measurement signal

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Passive Isolator DH 18 P–2

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-30-409982-0, Fax: +49-30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent