Tender Specification Isolation Amplifier DN 2000

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

9 versions available:

Isolation Amplifier, calibrated signal setting

Isolation and conversion of standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			0 - 20 mA, 4 - 20 mA, 0 - 10 V 
Output			0 - 20 mA, 4 - 20 mA, 0 - 10 V 
Range setting		simple selectable via DIP switches

Cut-off frequency	1 kHz, switchable to 30 Hz

Transmission error	< 0.1 % full scale

Power Supply		Universal power supply for 20 - 253 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		4 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Isolation Amplifier DN 2000 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Isolation Amplifier, fixed range: 0 - 20 mA to 0 - 20 mA, or 4 - 20 mA to 4 - 20 mA

Isolation and conversion of standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			0(4) - 20 mA 
Output			0(4) - 20 mA 
Cut-off frequency	1 kHz

Transmission error	< 0.1 % full scale

Power Supply		Universal power supply for 20 - 253 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		4 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Isolation Amplifier DN 2012 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Isolation Amplifier, fixed range: 4 - 20 mA to 0 - 20 mA

Isolation and conversion of standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			4 - 20 mA 
Output			0 - 20 mA 
Cut-off frequency	1 kHz

Transmission error	< 0.1 % full scale

Power Supply		Universal power supply for 20 - 253 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		4 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Isolation Amplifier DN 2032 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Isolation Amplifier, fixed range: 0 - 10 V to 0 - 20 mA

Isolation and conversion of standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			0 - 10 V 
Output			4 - 20 mA 
Cut-off frequency	1 kHz

Transmission error	< 0.1 % full scale

Power Supply		Universal power supply for 20 - 253 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		4 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Isolation Amplifier DN 2052 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Isolation Amplifier, fixed range: 0 - 20 mA to 4 - 20 mA

Isolation and conversion of standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			0 - 20 mA 
Output			4 - 20 mA 
Cut-off frequency	1 kHz

Transmission error	< 0.1 % full scale

Power Supply		Universal power supply for 20 - 253 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		4 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Isolation Amplifier DN 2014 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Isolation Amplifier, fixed range: 0 - 10 V to 4 - 20 mA

Isolation and conversion of standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			0 - 10 V 
Output			4 - 20 mA 
Cut-off frequency	1 kHz

Transmission error	< 0.1 % full scale

Power Supply		Universal power supply for 20 - 253 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		4 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Isolation Amplifier DN 2054 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Isolation Amplifier, fixed range: 0 - 20 mA to 0 - 10 V

Isolation and conversion of standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			0 - 20 mA 
Output			0 - 10 V 
Cut-off frequency	> 1 kHz

Transmission error	0.1 % of final value

Power Supply		Universal power supply for 20 - 253 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		4 kV, 50 Hz input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Isolation Amplifier DN 2016 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Isolation Amplifier, fixed range: 4 - 20 mA to 0 - 10 V

Isolation and conversion of standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			4 - 20 mA 
Output			0 - 10 V 
Cut-off frequency	> 1 kHz

Transmission error	0.1 % of final value

Power Supply		Universal power supply for 20 - 253 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		4 kV, 50 Hz input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Isolation Amplifier DN 2036 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Isolation Amplifier, fixed range: 0 - 10 V to 0 - 10 V

Isolation and conversion of standard signals,

slim housing for DIN-rail mounting, width 12.5 mm, protection class: IP 20

Input			0 - 10 V 
Output			0 - 10 V
Cut-off frequency	> 1 kHz

Transmission error	0.1 % of final value

Power Supply		Universal power supply for 20 - 253 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		4 kV, 50 Hz input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Isolation Amplifier DN 2056 AG

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent