Tender Specification Signal Splitter/Repeater DN 21000

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Signal Splitter/Repeater, calibrated signal setting

Conversion, isolation and distribution of standard signals,

slim housing for DIN-rail mounting, width 6.2 mm, protection class: IP 20

Input				0 - 20 mA, 4 - 20 mA
				0 - 10 V, 2 - 10 V, 0 - 5 V, 1 - 5 V'
Transmitter supply voltage	16 V
Output				0 - 20 mA, 4 - 20 mA 
				0 - 10 V, 2 - 10 V, 0 - 5 V, 1 - 5 V
Range setting			calibrated signal setting

Cut-off frequency		5 kHz

Transmission error		< 0.1 % of final value

Power supply			16.8 to 31.2 V DC, approx. 1.4 W, In-Rail-Bus

Protective separation		EN 61140, 4-Port isolation up to 300 V AC/DC between all circuits

Test voltage			3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage		600 V AC/DC for overvoltage category II and pollution degree 2

Type				Signal Splitter/Repeater DN 21000 ___	(see order code)

Supplier			DRAGO Automation GmbH, Berlin, Germany
				Phone: +49-30-409982-0, Fax: +49-30-409982-10, 
				email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code:

| Signal Splitter/Repeater, calibrated range selection | DN 21000 S |
| --- | --- |
| Signal Splitter/Repeater, calibrated range selection, In-Rail-Bus for power supply | DN 21000 B |