Tender Specification Temperature Transmitter DR 44

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Temperature Transmitter, fixed ranges

Temperature measuring with Pt 100 sensors,

slim housing for DIN-rail mounting, installation depth 60 mm, width 11.2 mm, protection class: IP 20

Input signal		Pt 100

Sensor connection: 4-wire

Measuring range within –100 °C to +450 °C, see order code

Measuring error		< 0.1 K + 0.05 % of span

Output			0 - 20 mA, 4 - 20 mA, 0 - 5 V, 1 - 5 V, 0 - 10 V, 2 - 10 V, see order code

Transmission error	< 0.1 % full scale

Zero/Span komp.	± 3 %

Response time		< 10 ms

Operation temeprature	–20 °C to +60 °C   (–4 °F to +140 °F)

Power supply		24 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Temperature Transmitter DR 44 P – __  __   (see order code)

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-30-409982-0, Fax: +49-30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code:

|  |  |  | Input | Output |
| --- | --- | --- | --- | --- |
| DR 44 P – |  |  | X | X |
| Input | 0 to +50 °C |  | 0 |  |
|  | 0 to +100 °C |  | 1 |  |
|  | 0 to +200 °C |  | 2 |  |
|  | 0 to +300 °C |  | 3 |  |
|  | 0 to +400 °C |  | 4 |  |
|  | –50 to +150 °C |  | 5 |  |
|  | –50 to +100 °C |  | 6 |  |
|  | –50 to +50 °C |  | 7 |  |
|  | further see Table |  | ? |  |
| Output | 0 - 20 mA |  |  | 2 |
|  | 4 - 20 mA |  |  | 4 |
|  | 0 - 5 V |  |  | 5 |
|  | 1 - 5 V |  |  | 8 |
|  | 0 - 10 V |  |  | 6 |
|  | 2 - 10 V |  |  | 7 |