Tender Specification Shunt/mV Isolation Amplifier DS 78

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Shunt/mV Isolation Amplifier, fixed setting

Cost optimized isolation and conversion of mV-shunt signals,

slim housing for DIN-rail mounting, installation depth 60 mm, width 11.2 mm, protection class: IP 20

Input			± 60 mV, ± 100 mV, ± 150 mV, ± 300 mV
			0 - 60 mV, 0 - 100 mV, 0 - 150 mV, 0 - 300 mV
			see Product line
Output			0 - 20 mA, 4 - 20 mA, 0 - 10 mA, 2 - 10 mA
			0 - 10 V, 2 - 10 V, 0 - 5 V, 1 - 5 V
			see Product line
Response time		2 ms

Transmission error	< 0.2 % full scale

Operation temeprature	–20 °C to +60 °C   (–4 °F to +140 °F)

Power supply		24 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Shunt/mV Isolation Amplifier DS 78 P – __  __  	(see Product line)

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-30-409982-0, Fax: +49-30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code:

|  |  |  | Input | Output |
| --- | --- | --- | --- | --- |
| DS 78 P – |  |  | X | Y |
| Input | ± 60 mV |  | 0 |  |
|  | 0 – 60 mV |  | 1 |  |
|  | ± 100 mV |  | 2 |  |
|  | 0 - 100 mV |  | 3 |  |
|  | ± 150 mV |  | 4 |  |
|  | 0 - 150 mV |  | 5 |  |
|  | ± 300 mV |  | 6 |  |
|  | 0 - 300 mV |  | 7 |  |
| Output | 0 - 10 V |  |  | 6 |
|  | 2 - 10 V |  |  | 7 |
|  | 0 - 5 V |  |  | 5 |
|  | 1 - 5 V |  |  | 8 |
|  | 0 - 20 mA |  |  | 2 |
|  | 4 - 20 mA |  |  | 4 |