Tender Specification Temperature Transmitter DT 45000

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Temperature Transmitter, programmable via USB and DIP switch

for Pt, Ni, KTY and TC Standard Sensors, resistance-, mV- and potentiometer measuring,

slim housing for DIN-rail mounting, width 6.2 mm, protection class: IP 20

Input			Pt 100 / Pt 200 / Pt 500 / Pt 1000, Sensor connection: 4-wire, 3-wire, 2-wire
			Ni 100 / Ni 200 / Ni 500 / Ni 1000, Sensor connection: 4-wire, 3-wire, 2-wire 
			Thermocouples Types B, E, J, K, L, N, R, S, T, U, W5Re_W26Re, W3Re_W25Re
			Cold junction comp.: internal, external, uncompensated, manual setting						min. Span: 50 K, depends on sensor type

Output (programmable)	0 to  20 mA, 4 to 20 mA, 0 to 5 V, 1 to 5 V, 0 to 10 V, 2 to 10 V, 0 to 10 mA, 2 to 10 mA
Transfer characteristic	Rising / falling linearly

Übertragungsfehler	< 0,1 % full scale

Messrate		4 / s

Hilfsenergie		9.6 to 31.2 V DC, approx. 0.8 W, In-Rail-Bus

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Typ			Temperature Transmitter DT 45000 ___		(see order code)

Supplier		DRAGO Automation GmbH, Berlin, Germany
			Tel.: +49-30-409982-0, Fax: +49-30-409982-10, 
			email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code:

| Temperature transmitter, programmable via USB and DIP switch | DT 45000 S |
| --- | --- |
| Temperature transmitter, programmable via USB and DIP switch, In-Rail-Bus for power supply | DT 45000 B |