Tender Specification Thermoelement Transmitter DT 45800

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Thermoelement Transmitter, configurable via DIP switch or USB

for nickel sensors,

slim housing for DIN-rail mounting, width 6.2 mm, protection class: IP 20

Input			Type K, J, A, B, C, D, E, L, N, R, S, T, U
			Cold junction compensation: Internal / OFF
			Error of Cold junction compensation < 1.5 K
			min. Span: 50 K, depends on sensor type
Measuring error		< 0.3 K + 0.08 % meas. value

Output (programmable)	0 to  20 mA, 4 to 20 mA, 0 to 5 V, 0 to 10 V 
Transfer characteristic	Rising / falling linearly

Übertragungsfehler	< 0.1 % full scale

Messrate		4 / s

Hilfsenergie		9.6 to 31.2 V DC, approx. 0.8 W, In-Rail-Bus

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Typ			Thermoelement Transmitter DT 45800 ___		(see order code)

Supplier		DRAGO Automation GmbH, Berlin, Germany
			Tel.: +49-30-409982-0, Fax: +49-30-409982-10, 
			email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code:

| Thermoelement transmitter, programmable via USB and DIP switch | DT 45800 S |
| --- | --- |
| Thermoelement transmitter, programmable via USB and DIP switch, In-Rail-Bus for power supply | DT 45800 B |